SERIES 4000 BVS OUTDOOR SAMPLER

Specification BVS-4300

PART 1: GENERAL

1.01	SUBMITTALS

A. 	Submit product literature that includes information on the performance and operation of the sampler, dimensions and weights, and functions of the controller.

B.	Upon request, provide shop drawings that clearly identify sampler dimensions and specifications.

1.02	QUALITY ASSURANCE

A.	Manufacturer shall have at least twenty (20) years experience in the production of effluent/liquid samplers, and shall provide references.

B.	Manufacturer shall have a CSA-certified shop in which they manufacture the samplers, and shall have the CSA sticker on the final product.

C.	Manufacturer shall be located within the USA or Canada.

PART 2: PRODUCTS

2.01	BVS OUTDOOR SAMPLER

A. 	Automatic Outdoor Wastewater Sampler shall be vacuum pump/compressor type with multi-function input controller, acrylic metering chamber, polypropylene sample containers, manufactured by Southwell Controls Ltd.

B.	Controller program types shall include composite, multi-composite, consecutive, daily cycle, and timed step.

C.	Controller shall be capable of initiating a sample via interval time, momentary external contact, integration of 4-20mA flow signal, pulse count or manual.

D.	Controller shall be capable of incorporating a start delay based on time/day using a real time clock, pulse count, integration of a 4-20mA flow signal, momentary external contact or level control (contact duration).

E.	Sampler shall be composite with samples deposited to a single sampler container; or discrete with samples deposited to multiple sample containers.

F.	500cc Metering chamber shall have 3/8” or 5/8” ID tubing inlet; 1000cc metering chamber shall have 3/8” ID tubing, 25 foot PVC intake tubing with SS sinker to be included.

G.	Sample compartment will be refrigerated or non-refrigerated, as required.

H.	Sampler shall include one 8L or one 20L polypropylene sample container for composite type or 24x500cc polypropylene containers for discrete type.

I.	Enclosure shall be NEMA 3 with optional insulation, powder coated steel or optional stainless steel.

J.	Sampler shall include slide-out instrument panel and tray with lockable door.

K.	Supply 115VAC, 10A power to sampler. All sampler components except refrigerator will be powered by 5VDC.

L.	Available options shall include pressure/vacuum gauge, heater with thermostat, overflow protection probes, common sampler fault output, external valve control output, SS sinker strainer, and internal battery with charger.

M.	Available optional materials shall include glass metering chamber, glass sample container(s), teflon chamber cover, Tygon inlet tubing and silicone discharge tubing.

2.02	FUNCTION

A.	Sampler is to be used for the purpose of taking liquid samples automatically for later laboratory analysis.

2.03	MANUFACTURER

A.	All samplers shall be of the series BVS 4300 as manufactured by Southwell Controls Ltd., in the USA or Canada, or approved equal.

PART 3: EXECUTION

3.01	INSTALLATION

A.	Sampler shall be installed in accordance with manufacturer’s written Instruction and Operation Manual.

3.02	MANUFACTURER’S WARRANTY AND CUSTOMER SERVICE

A.	Manufacturer’s authorized representative shall be available for customer service during installation and start-up, and to train personnel in the operation, maintenance and troubleshooting of the sampler.

B.	Manufacturer will give telephone support for troubleshooting or difficulties for the lifetime of the product.

C.	Sampler shall be under a two (2) year warranty for all parts.